PARTS & ILLUSTRATION

As shown: EST-NC & BST-NC - air connection at lower port

EAT & BAT - no spring, air connection at upper and lower port

ELT & BLT - no spring, air connection at upper port

EST-NO & BST-NO - spring under piston, air connection at upper port

F, BFS, & TUCA - see catalog for construction

GEON is a trademark of The Geon Company 	CORZAN is a trademark of The BF Goodrich Company

KYNAR is a trademark of Elf Atochem		VITON is a trademark of Dupont Company

1384 Pompton Avenue

Cedar Grove, NJ 07009-1095

( Telephone	(973) 256-3000

( Fax 		(973) 256-4745

( e-mail  info@plastomatic.com

I&MASO.doc  Rev. 17-Feb-05

AIR OPERATED VALVES

INSTALLATION, OPERATION, & MAINTENANCE INSTRUCTIONS

Series:

EAT & BAT - air pressure to open, air pressure to close

ELT & BLT - process inlet pressure to open, air pressure to close

EST-NC & BST-NC - air pressure to open, spring to close

EST-NO & BST-NO - spring to open,  air pressure to close

F, BFS, & TUCA - three way valve, air to actuate, spring return

IMPORTANT - BEFORE INSTALLING

Plast-O-Matic valves will operate reliably when properly installed and used within the recommended ranges of pressure, temperature, and chemical compatibility.  The ultimate determination of material compatibility is previous successful use in the same application.  Call our Technical Support for information about your application.

MATERIALS *

| NAME | CODE | COLOR | MAX. TEMP. |
| --- | --- | --- | --- |
| Geon/PVC | PV | DARK GRAY | 140 oF 60 oC |
| Corzan/CPVC | CP | LIGHT GRAY | 180 oF 80 oC |
| Polypropylene | PP | TRANSLUCENT WHITE | 180 oF 80 oC |
| GPP** | GPP | GREENISH OR WHITE | 220 oF 105 oC |
| Kynar/PVDF | PF | TRANSLUCENT WHITE (yellowish) | 280 oF 140 oC |
| PTFE | TF | OPAQUE WHITE | 300 oF 150 oC |
| Acrylic | PLEX | CLEAR | 160 oF 70 oC |
| Buna-N | B | BLACK | 200 oF 90 oC |
| EPDM | EP | BLACK | 250 oF 120 oC |
| Viton | V | BLACK OR BROWN | 300 oF 150 oC |

* Refer to Catalog ASO or TUCA for pressure ratings

**GPP = 20% glass filled polypropylene.

Minimum temperature 40oF (5oC).

Air pressure rating 100 PSI (actuation pressure only, these valves are not rated for gasses)  See catalog for air pressure requirements

INSTALLATION INSTRUCTIONS

Install the valve in the proper flow direction as indicated by the flow label.  The cylinder may be set in any position, vertical or horizontal.  Plast-O-Matic recommends upright for less strain on piping.

Caution: Plastic materials will degrade in ultraviolet (UV) light or sunlight.

Caution: Polypropylene and PVDF (Kynar) often look similar. Do not install in your system if you are not sure.

THREADED CONNECTION - Apply a suitable thread sealant (for example, PTFE tape) to male tapered threads. Assemble “hand-tight” followed by up to a quarter (1/4) turn with a strap wrench.  Do not over tighten or use pipe wrenches on plastic pipe and components.

Caution: PTFE tape will “string” as pipe threads are joined.  Loose “strings” could lie across the seating surface and prevent the valve from completely closing.  To avoid this problem, clean out old tape, and do not apply tape to the first thread.

Caution: Connect the valve to plastic pipe and fittings only; When using metal pipe or fittings, install with an intervening plastic fitting.  Metal pipe and straight threaded pipe will cut, stretch, and distort the plastic bodies, which could result in cracking or leaking over time.

NON-THREADED CONNECTIONS - For solvent cementing or heat fusion, follow instructions supplied with the cement or fusion equipment, or contact your distributor.  Take care to avoid dripping cement into the valve.

MOUNTING - These valves are designed to be supported by the piping.  The piping must be properly supported, taking into account the weight of the valve, piping, and process liquid.

AIR CONNECTION --  Recommended air pressure for actuation is  65 to 100 PSI  (5 to 7 bar).   The air should be filtered, regulated, and lubricated, with no solvent vapors or detergents, for longer service life.

OPERATION

MAINTENANCE

REPLACEMENT SEAL KIT - Plast-O-Matic recommends keeping a spare seal kit available for repairs.  Seal life will vary in applications due to cycles, temperatures, pressures, chemicals, and concentration. Based on the application, a periodic inspection and maintenance plan should be established.  The seal kit part number is “SK” plus the part number less the material suffix.  For example, the seal kit for BAT050V-PV is SKBAT050V.

FAIL DRY( - A vent port is provided on some models to protect the spring from contact with the liquid.  If there is a failure of the primary seals, secondary seals protect the valve, and the leaking liquid drains out through the Fail Dry vent.  If your valve has a threaded port, you can run a line from the port to an open drain or containment.