Product Guarantee

Plast-O-Matic guarantees its products to be free from defects in material or workmanship over a period of one (1) year from date of shipment from its factory.

If any product is found unsatisfactory under this Guarantee, the purchaser should notify Plast-O-Matic in writing or phone, and after receipt of Plast-O-Matic’s shipping approval, the purchaser may return it directly to Plast-O-Matic’s factory in New Jersey (USA), shipping charges prepaid.

Such products will be inspected by Plast-O-Matic and if determined defective due to material or workmanship shall be replaced or put in proper operating condition, free of all charges, including ground freight, and a credit will be allowed for ground freight to Plast-O-Matic. The correction of any defects by repair or replacement by Plast-O-Matic shall constitute fulfillment of all obligations and liability of Plast-O-Matic to the purchaser under this Guarantee.

Plast-O-Matic is not responsible for damage to its products through improper installation, maintenance, use or attempts to operate it beyond its mechanical or electrical capacity intentionally or otherwise, or for unauthorized repair including freight charges.

Any failure to notify Plast-O-Matic immediately of unsatisfactory operation, or any improper or unauthorized installation, maintenance, use, repair or adjustments, shall terminate this Guarantee and shall relieve Plast-O-Matic from any further responsibility thereunder.

Plast-O-Matic shall not be liable for special or consequential damages in any claim, action, suit, or proceedings arising under this Guarantee, nor shall there be any liability thereunder for claims for labor, loss or profit or good will, repairs or other expenses incidental  to replacement.

The foregoing warranty is exclusive and in lieu of any and all other warranties, expressed or implied. No warranty of merchantability, no implied warranty of fitness for any particular purpose, and no implied warranty arising by usage of trade, course of dealing or course of performance is given by seller or shall arise by or in connection with this sale and/or the seller’s and/or buyer’s conduct in relation thereto or to each other, and in no event shall seller be liable on any such warranty with respect to any product.

PYREX is a trademark of Corning Glass

KYNAR is a trademark of Elf Atochem

TEFLON is a trademark of Dupont Company

PLAST-O-MATIC VALVES, INC.

1384 Pompton Avenue

Cedar Grove, NJ 07009-1095

( Telephone	(973) 256-3000

( Fax 		(973) 256-4745

( e-mail  info@plastomatic.com

I&MGX.doc  Rev. 3-May-99

Series GL, GX, GY, GYW, & GYWX

Chemical Flow and Level Indicators

(Sight Glasses)

INSTALLATION & MAINTENANCE INSTRUCTIONS

IMPORTANT - BEFORE INSTALLING

Plast-O-Matic sight glasses will provide visual indication of flow or level when properly installed and used within the recommended ranges of pressure, temperature, and chemical compatibility.  Pyrex® will etch when in contact with concentrated solutions of hydrofluoric acid (HF) or caustic soda (NaOH) and is not recommended for these applications. The ultimate determination of material compatibility is previous successful use in the same application.  Call our Technical Support for information about your application.

Caution: Plastic materials will degrade in ultraviolet (UV) light or sunlight.

Caution: Polypropylene and PVDF (Kynar®) often look similar. Do not install in your system if you are not sure.

Material Reference:

Material	P/N Suffix	Color		Maximum Temperature

PVC		-PV		Dark Gray		140 ºF (60 ºC)

CPVC		-CP		Light Gray		180 ºF (80 ºC)

Polypropylene	-PP		Translucent White	180 ºF (80 ºC)

PTFE (Teflon®)	-TF		Solid White		225 ºF (107 ºC)

PVDF (Kynar)	-PF		Orangeish White	293 ºF (145 ºC)

EPDM seals limited to 250 ºF (120 ºC), Buna-N to 200 ºF (95 ºC).

Minimum temperature 40 ºF (5 ºC).

See the Product Data Sheet or consult our Technical Support staff for pressure ratings or other information.

INSTALLATION INSTRUCTIONS

THREADED CONNECTION - Apply a suitable thread sealant (for example, Teflon tape) to male tapered threads to assure a “leak-tight” seal.  Assemble “hand-tight” followed by a quarter (1/4) turn with a strap wrench.  Do not over tighten or use pipe wrenches on plastic pipe and components.

Caution: Teflon tape will “string” as pipe threads are joined.  Loose “strings” could lie across the seating surface and prevent the valve from completely closing.  To avoid this problem, clean out old tape, and do not apply tape to the first thread.

Caution: Connect to plastic pipe and fittings only; when using metal pipe, install an intervening plastic fitting.  Metal pipe and straight threaded pipe tends to cut, stretch, and distort the plastic bodies, resulting in cracking or leaking over time.

NON-THREADED CONNECTIONS - For solvent cementing or heat fusion, follow the instructions supplied with the cement or fusion equipment, or contact your distributor.

PARTS & ILLUSTRATION

When streamers or fluttering devices are installed, the sight glass must be installed in the proper flow direction so that the flow indication is visible.

Bolts should be carefully tightened by hand before using wrenches to make sure that there is no misalignment, and the assembly is evenly stressed.  Tighten bolts (alternating sides) with a torque wrench to 10 to 15 foot pounds (15 to 20 N-m)

Series GL typical installation includes two ball valves (not included) for easy service.  Overlap sighting area for continuous level indication with no visual dead spots.  Do not series connect level indicators with pipe nipples because the assembly will be unstable and a visual dead spot will be created.